## Lines
Status: 31.12.2024 |  |  | Substation_1 |  | Substation_2 |  |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters
NE_name | EIC_Code | TSO | Full_name | Short_name | Full_name | Short_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Eula - Röhrsdorf 203 | 11TD8L203------C | 50HERTZ | Eula | D8EU__2 | Röhrsdorf | D8ROE_2 | 220 | [6 empty] | 790 |  |  | 4.0937 | 18.349 | 161.1637 | 51.511
Röhrsdorf - Weida 207 | 11TD8L207------H | 50HERTZ | Röhrsdorf | D8ROE_2 | Weida | D8WD__2 | 220 | [6 empty] | 790 |  |  | 7.5895 | 31.888 | 348.7168 | 98.324
Eula - Weida 208 | 11TD8L208------9 | 50HERTZ | Eula | D8EU__2 | Weida | D8WD__2 | 220 | [6 empty] | 1070 |  |  | 5.0537 | 19.541 | 264.2394 | 67.55
Bentwisch - Güstrow 275 | 11TD8L275------7 | 50HERTZ | Bentwisch | D8BW__2 | Güstrow | D8GUE_2 | 220 | [6 empty] | 1200 |  |  | 1.909 | 12.055 | 158.0849 | 41.418
Wuhlheide - Thyrow 291 | 11TD8L291------L | 50HERTZ | Wuhlheide | D8WUH_2 | Thyrow | D8THY_2 | 220 | [6 empty] | 960 |  |  | 2.9672 | 11.191 | 266.784 | 38.882
Neuenhagen - Hennigsdorf 293 | 11TD8L293------5 | 50HERTZ | Neuenhagen | D8NHG_2 | Hennigsdorf | D8HEN_2 | 220 | [6 empty] | 1070 |  |  | 1.644 | 11.984 | 215.89 | 46.429
Neuenhagen - Wustermark 294 | 11TD8L294------Y | 50HERTZ | Neuenhagen | D8NHG_2 | Wustermark | D8WU__2 | 220 | [6 empty] | 900 |  |  | 1.426 | 17.532 | 326.317 | 68.9
Hennigsdorf - Wustermark 295 | 11TD8L295------Q | 50HERTZ | Hennigsdorf | D8HEN_2 | Wustermark | D8WU__2 | 220 | [6 empty] | 1070 |  |  | 0.655 | 7.053 | 129.496 | 27.531
Marzahn - Wuhlheide 301 | 11TD8L301------I | 50HERTZ | Marzahn | D8MZA_2 | Wuhlheide | D8WUH_2 | 220 | [6 empty] | 1070 |  |  | 0.5487 | 2.4908 | 37.0708 | 9.111
Marzahn - Wuhlheide(Abzweig) 302/1 | 11TD8L302------A | 50HERTZ | Marzahn | D8MZA_2 | Wuhlheide (Abzweig) | D8WUH_2 | 220 | [6 empty] | 960 |  |  | 0.545 | 2.4772 | 37.0708 | 9.111
Wuhlheide (Abzweig) - Thyrow 302/2 | 11TD8L302------A | 50HERTZ | Wuhlheide (Abzweig) | D8WUH_2 | Thyrow | D8THY_2 | 220 | [6 empty] | 960 |  |  | 2.9672 | 11.191 | 153.1212 | 38.882
Lubmin - Lüdershagen 313 | 11TD8L313------U | 50HERTZ | Lubmin | D8LUB_2 | Lüdershagen | D8LHG_2 | 220 | [6 empty] | 1200 |  |  | 2.821 | 16.33 | 214.3823 | 56.212
Lubmin - Lüdershagen 314 | 11TD8L314------M | 50HERTZ | Lubmin | D8LUB_2 | Lüdershagen | D8LHG_2 | 220 | [6 empty] | 1200 |  |  | 2.821 | 16.33 | 214.3823 | 56.212
Pasewalk - Güstrow 315 | 11TD8L315------E | 50HERTZ | Pasewalk | D8PAS_2 | Güstrow | D8GUE_2 | 220 | [6 empty] | 900 |  |  | 12.1223 | 44.3118 | 572.3982 | 151.143
Pasewalk - Güstrow 316 | 11TD8L316------6 | 50HERTZ | Pasewalk | D8PAS_2 | Güstrow | D8GUE_2 | 220 | [6 empty] | 900 |  |  | 12.1223 | 44.3118 | 572.3982 | 151.143
Lüdershagen - Güstrow 317-276 | 11TD8L317-276--N | 50HERTZ | Lüdershagen | D8LHG_2 | Güstrow | D8GUE_2 | 220 | [6 empty] | 1200 |  |  | 6.59 | 31.384 | 404.4486 | 106.538
Lüdershagen - Bentwisch 318 | 11TD8L318------R | 50HERTZ | Lüdershagen | D8LHG_2 | Bentwisch | D8BW__2 | 220 | [6 empty] | 1200 |  |  | 4.69 | 19.401 | 247.3376 | 65.349
Parchim/Süd - Güstrow 328 | 11TD8L328------I | 50HERTZ | Parchim/Süd | D8PMS_2 | Güstrow | D8GUE_2 | 220 | [6 empty] | 900 |  |  | 15.5033 | 57.559 | 196.2239 | 52.317
Parchim/Süd - Wolmirstedt 332-322 | 11TD8L332-322--6 | 50HERTZ | Parchim/Süd | D8PMS_2 | Wolmirstedt | D8WOL_2 | 220 | [6 empty] | 900 |  |  | 6.954 | 37.594 | 605.982 | 140.903
Eula - Wolkramshausen 357 | 11TD8L357-----0Y | 50HERTZ | Eula | D8EU__2 | Wolkramshausen | D8WK__2 | 220 | [6 empty] | 1070 |  |  | 12.208 | 46.854 | 600.0442 | 159.147
Eula - Wolkramshausen 358 | 11TD8L358------S | 50HERTZ | Eula | D8EU__2 | Wolkramshausen | D8WK__2 | 220 | [6 empty] | 1070 |  |  | 12.208 | 46.854 | 600.0442 | 159.147
Vieselbach - Wolkramshausen 367 | 11TD8L367------R | 50HERTZ | Vieselbach | D8VIB_2 | Wolkramshausen | D8WK__2 | 220 | [6 empty] | 1600 |  |  | 2.5437 | 19.586 | 245.6725 | 65.756
Vieselbach - Wolkramshausen 368 | 11TD8L368------J | 50HERTZ | Vieselbach | D8VIB_2 | Wolkramshausen | D8WK__2 | 220 | [6 empty] | 1600 |  |  | 2.5437 | 19.586 | 245.6725 | 65.756
Wustermark - Thyrow 526 | 11TD8L526------E | 50HERTZ | Wustermark | D8WU__2 | Thyrow | D8THY_2 | 220 | [6 empty] | 1290 |  |  | 2.0631 | 17.306 | 312.5256 | 69.44
Vieselbach - Remptendorf - Großschwabhausen 415 | 11TD8L415------4 | 50HERTZ | Vieselbach | D8VIB_1 | Remptendorf - Großschwabhausen | D8RE__1 | 380 | [6 empty] | 2720 |  |  | 3.004 | 19.631 | 338.0982 | 77.547
Vieselbach - Remptendorf 416 | 11TD8L416------X | 50HERTZ | Vieselbach | D8VIB_1 | Remptendorf | D8RE__1 | 380 | [6 empty] | 2720 |  |  | 3.0161 | 19.711 | 339.5433 | 77.547
Krümmel - Görries 419 | 11TD8L419------9 | 50HERTZ | Krümmel | D8KRU_1 | Görries | D8GOE_1 | 380 | [6 empty] | 2700 |  |  | 2.2112 | 22.407 | 389.0863 | 87.47
Krümmel - Wessin 420 | 11TD8L420------Z | 50HERTZ | Krümmel | D8KRU_1 | Wessin | D8WE__1 | 380 | [6 empty] | 2700 |  |  | 2.9614 | 28.516 | 495.7119 | 111.421
Görries - Güstrow 423 | 11TD8L423------B | 50HERTZ | Görries | D8GOE_1 | Güstrow | D8GUE_1 | 380 | [6 empty] | 2720 |  |  | 2.2401 | 18.244 | 311.9916 | 71.582
Wessin - Güstrow 424 | 11TD8L424------3 | 50HERTZ | Wessin | D8WE__1 | Güstrow | D8GUE_1 | 380 | [6 empty] | 2720 |  |  | 1.4741 | 12.006 | 205.2402 | 47.103
Wolmirstedt - Förderstedt 437 | 11TD8L437------7 | 50HERTZ | Wolmirstedt | D8WOL_1 | Förderstedt | D8FOE_1 | 380 | [6 empty] | 2520 |  |  | 1.3442 | 12.79 | 209.554 | 48.545
Wolmirstedt - Förderstedt 438 | 11TD8L438-----0Y | 50HERTZ | Wolmirstedt | D8WOL_1 | Förderstedt | D8FOE_1 | 380 | [6 empty] | 2520 |  |  | 1.3442 | 12.79 | 209.576 | 48.545
Eisenach - Vieselbach 454 | 11TD8L454------D | 50HERTZ | Eisenach | D8EI__1 | Vieselbach | D8VIB_1 | 380 | [6 empty] | 2520 |  |  | 1.891 | 18.946 | 306.5252 | 72.285
Altenfeld - Remptendorf 463 | 11TD8L463------C | 50HERTZ | Altenfeld | D8ATF_1 | Remptendorf | D8RE__1 | 380 | [6 empty] | 2370 |  |  | 1.4946 | 13.5377 | 208.5389 | 50.254
Altenfeld - Remptendorf 464 | 11TD8L464------4 | 50HERTZ | Altenfeld | D8ATF_1 | Remptendorf | D8RE__1 | 380 | [6 empty] | 2370 |  |  | 1.4946 | 13.5377 | 208.5389 | 50.254
Vieselbach - Altenfeld 467 | 11TD8L467------H | 50HERTZ | Vieselbach | D8VIB_1 | Altenfeld | D8ATF_1 | 380 | [6 empty] | 3600 |  |  | 1.1669 | 14.503 | 267.6637 | 56.081
Vieselbach - Altenfeld 468 | 11TD8L468------9 | 50HERTZ | Vieselbach | D8VIB_1 | Altenfeld | D8ATF_1 | 380 | [6 empty] | 3600 |  |  | 1.1669 | 14.503 | 267.6637 | 56.081
Lauchstädt - Vieselbach 471 | 11TD8L471------J | 50HERTZ | Lauchstädt | D8LAU_1 | Vieselbach | D8VIB_1 | 380 | [6 empty] | 3600 |  |  | 1.4276 | 19.656 | 358.456 | 78.069
Lauchstädt - Vieselbach 472 | 11TD8L472------B | 50HERTZ | Lauchstädt | D8LAU_1 | Vieselbach | D8VIB_1 | 380 | [6 empty] | 3600 |  |  | 1.4276 | 19.656 | 361.597 | 78.069
Lubmin - Altentreptow/Nord 475 | 11TD8L475------O | 50HERTZ | Lubmin | D8LUB_1 | Altentreptow/Nord | D8ATN_1 | 380 | [6 empty] | 2520 |  |  | 1.4206 | 13.747 | 219.5659 | 52.115
Lubmin - Altentreptow/Süd 476 | 11T0-0000-0007-7 | 50HERTZ | Lubmin | D8LUB_1 | Altentreptow/Süd | D8ATS_1 | 380 | [6 empty] | 2520 |  |  | 1.622 | 17.826 | 290.2832 | 68.8
Altentreptow/Nord - Altentreptow/Süd 477 | 11T0-0000-0008-4 | 50HERTZ | Altentreptow/Nord | D8ATN_1 | Altentreptow/Süd | D8ATS_1 | 380 | [6 empty] | 2520 |  |  | 0.395 | 4.342 | 70.7801 | 16.767
Altentreptow/Süd - Gransee 479 | 11T0-0000-0009-1 | 50HERTZ | Altentreptow/Süd | D8ATS_1 | Gransee | D8GSE_1 | 380 | [6 empty] | 2520 |  |  | 1.814 | 19.938 | 325.2491 | 77.008
Stendal/West - Wolmirstedt 488 | 11T0-0000-0980-P | 50HERTZ | Stendal/West | D8STW_1 | Wolmirstedt | D8WOL_1 | 380 | [6 empty] | 3600 |  |  | 0.58458 | 9.2916 | 172.4734 | 37.245
Stendal/West - Wolmirstedt 489 | 11TD8L489------K | 50HERTZ | Stendal/West | D8STW_1 | Wolmirstedt | D8WOL_1 | 380 | [6 empty] | 2520 |  |  | 1.1824 | 9.63 | 160.8181 | 37.245
Stendal/West - Wolmirstedt 490 | 11TD8L490------9 | 50HERTZ | Stendal/West | D8STW_1 | Wolmirstedt | D8WOL_1 | 380 | [6 empty] | 2520 |  |  | 1.1824 | 9.63 | 160.8181 | 37.245
Wolmirstedt - Teufelsbruch 493 | 11TD8L493------M | 50HERTZ | Wolmirstedt | D8WOL_1 | Teufelsbruch | D8TB__1 | 380 | [6 empty] | 2400 |  |  | 3.6651 | 33.198 | 518.6769 | 124.397
Wolmirstedt - Wustermark 494 | 11TD8L494------E | 50HERTZ | Wolmirstedt | D8WOL_1 | Wustermark | D8WU__1 | 380 | [6 empty] | 2500 |  |  | 3.1838 | 27.944 | 434.4194 | 104.103
Neuenhagen - Marzahn 495 | 11TD8L495------6 | 50HERTZ | Neuenhagen | D8NHG_1 | Marzahn | D8MZA_1 | 380 | [6 empty] | 2280 |  |  | 0.7606 | 4.3135 | 71.9425 | 16.937
Neuenhagen - Marzahn 496 | 11TD8L496------Z | 50HERTZ | Neuenhagen | D8NHG_1 | Marzahn | D8MZA_1 | 380 | [6 empty] | 2400 |  |  | 0.7606 | 4.3135 | 71.9425 | 16.937
Wustermark - Teufelsbruch 498 | 11TD8L498------J | 50HERTZ | Wustermark | D8WU__1 | Teufelsbruch | D8TB__1 | 380 | [6 empty] | 2400 |  |  | 0.7176 | 7.7358 | 129.8106 | 29.597
Jessen/Nord - Lauchstädt 499 | 11TD8L499------B | 50HERTZ | Jessen/Nord | D8JSN_1 | Lauchstädt | D8LAU_1 | 380 | [6 empty] | 2040 |  |  | 3.3388 | 25.4187 | 464.5787 | 102.157
Jessen/Nord - Marke 500 | 11TD8L500------6 | 50HERTZ | Jessen/Nord | D8JSN_1 | Marke | D8MA__1 | 380 | [6 empty] | 2040 |  |  | 3.4508 | 26.8854 | 490.5911 | 107.37
Ragow - Schönewalde 501 | 11T0-0000-0040-C | 50HERTZ | Ragow | D8RAG_1 | Schönewalde | D8SW__1 | 380 | [6 empty] | 2040 |  |  | 1.6985 | 13.4421 | 246.772 | 54.003
Ragow - Jessen/Nord 502 | 11TD8L502-----1N | 50HERTZ | Ragow | D8RAG_1 | Jessen/Nord | D8JSN_1 | 380 | [6 empty] | 2040 |  |  | 1.945 | 15.45 | 290.28 | 61.782
Schönewalde - Jessen/Nord 503 | 11TD8L503-----1F | 50HERTZ | Schönewalde | D8SW__1 | Jessen/Nord | D8JSN_1 | 380 | [6 empty] | 2040 |  |  | 0.25355 | 2.0615 | 36.2854 | 7.953
Marke - Lauchstädt 504 | 11TD8L504------B | 50HERTZ | Marke | D8MA__1 | Lauchstädt | D8LAU_1 | 380 | [6 empty] | 2040 |  |  | 2.104 | 12.729 | 230.1531 | 50.873
Lubmin - Siedenbrünzow 509 | 11TD8L509------8 | 50HERTZ | Lubmin | D8LUB_1 | Siedenbrünzow | D8SOW_1 | 380 | [6 empty] | 2520 |  |  | 1.5903 | 14.442 | 243.1279 | 56.205
Lubmin - Siedenbrünzow 510 | 11TD8L510------Y | 50HERTZ | Lubmin | D8LUB_1 | Siedenbrünzow | D8SOW_1 | 380 | [6 empty] | 2520 |  |  | 1.5903 | 14.442 | 243.1279 | 56.205
Siedenbrünzow - Güstrow 512 | 11TD8L512-----1E | 50HERTZ | Siedenbrünzow | D8SOW_1 | Güstrow | D8GUE_1 | 380 | [6 empty] | 2500 |  |  | 3.3653 | 25.045 | 386.9186 | 93.611
Siedenbrünzow - Putlitz/Süd 513 | 11TD8L513-----16 | 50HERTZ | Siedenbrünzow | D8SOW_1 | Putlitz/Süd | D8PZS_1 | 380 | [6 empty] | 2500 |  |  | 2.589 | 28.065 | 464.5787 | 109.1
Güstrow - Putlitz/Süd 514 | 11TD8L514-----1Z | 50HERTZ | Güstrow | D8GUE_1 | Putlitz/Süd | D8PZS_1 | 380 | [6 empty] | 2520 |  |  | 2.882 | 26.429 | 422.23 | 100.3
Perleberg - Stendal/West 516 | 11TD8L516------N | 50HERTZ | Perleberg | D8PE__1 | Stendal/West | D8STW_1 | 380 | [6 empty] | 2520 |  |  | 2.4508 | 19.375 | 324.7778 | 75.543
Gransee - Neuenhagen 517 | 11TD8L517-----1B | 50HERTZ | Gransee | D8GSE_1 | Neuenhagen | D8NHG_1 | 380 | [6 empty] | 2040 |  |  | 1.659 | 18.225 | 296.4093 | 70.32
Altentreptow/Süd - Malchow 518 | 11T0-0000-0010-O | 50HERTZ | Altentreptow/Süd | D8ATS_1 | Malchow | D8MOW_1 | 380 | [6 empty] | 2040 |  |  | 3.09 | 33.95 | 553.2345 | 131.262
Neuenhagen - Malchow 520 | 11TD8L520------P | 50HERTZ | Neuenhagen | D8NHG_1 | Malchow | D8MOW_1 | 380 | [6 empty] | 2040 |  |  | 0.5655 | 6.2143 | 101.1279 | 23.992
Wustermark - Ragow 521-525 | 11TD8L521-525--G | 50HERTZ | Wustermark | D8WU__1 | Ragow | D8RAG_1 | 380 | [6 empty] | 2504 |  |  | 4.0033 | 32.625 | 585.4358 | 130.739
Thyrow - Ragow 522 | 11TD8L522------9 | 50HERTZ | Thyrow | D8THY_1 | Ragow | D8RAG_1 | 380 | [6 empty] | 2504 |  |  | 1.9479 | 15.382 | 277.9681 | 61.804
Ragow - Jessen/Nord 531 | 11T0-0000-0041-9 | 50HERTZ | Ragow | D8RAG_1 | Jessen/Nord | D8JSN_1 | 380 | [6 empty] | 2520 |  |  | 1.8259 | 17.1078 | 290.974 | 65.743
Förderstedt - Jessen/Nord 533 | 11T0-0000-0042-6 | 50HERTZ | Förderstedt | D8FOE_1 | Jessen/Nord | D8JSN_1 | 380 | [6 empty] | 2520 |  |  | 3.2516 | 30.4911 | 527.0964 | 117.5
Klostermansfeld - Wolmirstedt 535 | 11T0-0000-2052-R | 50HERTZ | Klostermansfeld | D8KLM_1 | Wolmirstedt | D8WOL_1 | 380 | [6 empty] | 2520 |  |  | 3.877 | 30.268 | 526.531 | 117.068
Wolmirstedt - Klostermansfeld 536 | 11TD8L536------5 | 50HERTZ | Wolmirstedt | D8WOL_1 | Klostermansfeld | D8KLM_1 | 380 | [6 empty] | 2520 |  |  | 3.878 | 30.276 | 526.657 | 117.096
Lauchstädt - Klostermansfeld 537 | 11T0-0000-2053-O | 50HERTZ | Lauchstädt | D8LAU_1 | Klostermansfeld | D8KLM_1 | 380 | [6 empty] | 2520 |  |  | 1.375 | 10.038 | 174.515 | 38.731
Klostermansfeld - Lauchstädt 538 | 11TD8L538------Q | 50HERTZ | Klostermansfeld | D8KLM_1 | Lauchstädt | D8LAU_1 | 380 | [6 empty] | 2520 |  |  | 1.375 | 10.04 | 174.233 | 38.738
Ragow - Preilack 539 | 11TD8L539------I | 50HERTZ | Ragow | D8RAG_1 | Preilack | D8PRL_1 | 380 | [6 empty] | 2280 |  |  | 1.3485 | 10.826 | 191.5743 | 43.164
Ragow - Preilack 540 | 11TD8L540------7 | 50HERTZ | Ragow | D8RAG_1 | Preilack | D8PRL_1 | 380 | [6 empty] | 2280 |  |  | 1.3485 | 10.826 | 191.5743 | 43.164
Graustein - Preilack 541 | 11TD8L541-----0Y | 50HERTZ | Graustein | D8GRS_1 | Preilack | D8PRL_1 | 380 | [6 empty] | 2000 |  |  | 2.0053 | 15.874 | 269.1402 | 62.459
Graustein - Preilack 542 | 11TD8L542------S | 50HERTZ | Graustein | D8GRS_1 | Preilack | D8PRL_1 | 380 | [6 empty] | 2000 |  |  | 2.0053 | 15.874 | 269.1402 | 62.459
Bentwisch - Güstrow 543 | 11TD8L543------K | 50HERTZ | Bentwisch | D8BW__1 | Güstrow | D8GUE_1 | 380 | [6 empty] | 2720 |  |  | 0.9146 | 9.0037 | 157.331 | 35.561
Bentwisch - Güstrow 544 | 11TD8L544------C | 50HERTZ | Bentwisch | D8BW__1 | Güstrow | D8GUE_1 | 380 | [6 empty] | 2720 |  |  | 0.9146 | 9.0037 | 157.331 | 35.561
Eisenhüttenstadt (Abzweig) - Eisenhüttenstadt 547-3 | 11TD8L547------P | 50HERTZ | Eisenhüttenstadt (Abzweig) | D8EHH_1 | Eisenhüttenstadt | D8EH__1 | 380 | [6 empty] | 1200 |  |  | 0.502 | 1.818 | 34.6204 | 7.526
Eisenhüttenstadt (Abzweig) - Preilack 547-2 | 11TD8L547------P | 50HERTZ | Eisenhüttenstadt (Abzweig) | D8EHH_1 | Preilack | D8PRL_1 | 380 | [6 empty] | 2280 |  |  | 1.422 | 9.63 | 170.8712 | 38.476
Eisenhüttenstadt (Abzweig) - Neuenhagen 547-1 | 11TD8L547------P | 50HERTZ | Eisenhüttenstadt (Abzweig) | D8EHH_1 | Neuenhagen | D8NHG_1 | 380 | [6 empty] | 2280 |  |  | 3.2182 | 21.7937 | 404.0088 | 87.005
Eisenhüttenstadt (Abzweig) - Eisenhüttenstadt 548-3 | 11T0000000000023 | 50HERTZ | Eisenhüttenstadt (Abzweig) | D8EHH_1 | Eisenhüttenstadt | D8EH__1 | 380 | [6 empty] | 1200 |  |  | 0.502 | 1.818 | 34.6204 | 7.526
Eisenhüttenstadt (Abzweig) - Preilack 548-2 | 11T0000000000023 | 50HERTZ | Eisenhüttenstadt (Abzweig) | D8EHH_1 | Preilack | D8PRL_1 | 380 | [6 empty] | 2280 |  |  | 1.422 | 9.63 | 170.8712 | 38.476
Heinersdorf - Neuenhagen 444 | 11T0000000000015 | 50HERTZ | Heinersdorf | D8HND_1 | Neuenhagen | D8NHG_1 | 380 | [6 empty] | 2280 |  |  | 1.5429 | 10.4487 | 185.071 | 41.71
Eisenhüttenstadt (Abzweig) - Heinersdorf 548-4 | 11T0000000000023 | 50HERTZ | Eisenhüttenstadt (Abzweig) | D8EHH_1 | Heinersdorf | D8HND_1 | 380 | [6 empty] | 2280 |  |  | 1.674 | 11.334 | 200.7478 | 45.247
Bärwalde - Schmölln 551 | 11TD8L551------R | 50HERTZ | Bärwalde | D8BAE_1 | Schmölln | D8SM__1 | 380 | [6 empty] | 3600 |  |  | 0.7441 | 11.506 | 218.969 | 45.911
Bärwalde - Schmölln 552 | 11TD8L552------J | 50HERTZ | Bärwalde | D8BAE_1 | Schmölln | D8SM__1 | 380 | [6 empty] | 3600 |  |  | 0.7441 | 11.506 | 218.969 | 45.911
Hagenwerder - Schmölln 553 | 11TD8L553------B | 50HERTZ | Hagenwerder | D8HGW_1 | Schmölln | D8SM__1 | 380 | [6 empty] | 2500 |  |  | 1.6516 | 14.496 | 252.3013 | 56.656
Hagenwerder - Schmölln 554 | 11TD8L554------3 | 50HERTZ | Hagenwerder | D8HGW_1 | Schmölln | D8SM__1 | 380 | [6 empty] | 2500 |  |  | 1.6516 | 14.496 | 252.3013 | 56.656
Schmölln - Dresden/Süd 555 | 11TD8L555------W | 50HERTZ | Schmölln | D8SM__1 | Dresden/Süd | D8DRS_1 | 380 | [6 empty] | 2500 |  |  | 1.0031 | 9.3866 | 163.0487 | 36.548
Schmölln - Dresden/Süd 556 | 11TD8L556------O | 50HERTZ | Schmölln | D8SM__1 | Dresden/Süd | D8DRS_1 | 380 | [6 empty] | 2500 |  |  | 1.0031 | 9.3866 | 163.0487 | 36.548
Bärwalde - Streumen 557 | 11TD8L557------G | 50HERTZ | Bärwalde | D8BAE_1 | Streumen | D8STR_1 | 380 | [6 empty] | 2520 |  |  | 2.5843 | 24.182 | 404.3544 | 93.783
Bärwalde - Streumen 558 | 11TD8L558------8 | 50HERTZ | Bärwalde | D8BAE_1 | Streumen | D8STR_1 | 380 | [6 empty] | 2520 |  |  | 2.5843 | 24.182 | 404.3544 | 93.783
Preilack - Altdöbern 559 | 11T0-0000-0948-H | 50HERTZ | Preilack | D8PRL_1 | Altdöbern | D8ADB_1 | 380 | [6 empty] | 2040 |  |  | 1.2462 | 13.4333 | 224.099 | 50.505
Preilack - Streumen 560 | 11TD8L560------Q | 50HERTZ | Preilack | D8PRL_1 | Streumen | D8STR_1 | 380 | [6 empty] | 2040 |  |  | 3.0048 | 32.391 | 537.904 | 121.222
Ragow - Streumen 561 | 11T0-0000-0043-3 | 50HERTZ | Ragow | D8RAG_1 | Streumen | D8STR_1 | 380 | [6 empty] | 2504 |  |  | 2.9365 | 22.6101 | 385.0022 | 88.719
Ragow - Streumen 562 | 11TD8L562------A | 50HERTZ | Ragow | D8RAG_1 | Streumen | D8STR_1 | 380 | [6 empty] | 2504 |  |  | 2.9365 | 22.6101 | 385.0022 | 88.719
Graustein - Bärwalde 565 | 11TD8L565------N | 50HERTZ | Graustein | D8GRS_1 | Bärwalde | D8BAE_1 | 380 | [6 empty] | 2520 | 2520 | 3150 | 0.6666 | 5.5904 | 96.4155 | 21.801
Graustein - Bärwalde 566 | 11TD8L566------F | 50HERTZ | Graustein | D8GRS_1 | Bärwalde | D8BAE_1 | 380 | [6 empty] | 2520 | 2520 | 3150 | 0.6666 | 5.5904 | 96.4155 | 21.801
Streumen - Röhrsdorf 571 | 11TD8L571------9 | 50HERTZ | Streumen | D8STR_1 | Röhrsdorf | D8ROE_1 | 380 | [6 empty] | 2504 | 2504 | 3150 | 2.6478 | 19.844 | 385.7876 | 82.808
Streumen - Röhrsdorf 572 | 11TD8L572------1 | 50HERTZ | Streumen | D8STR_1 | Röhrsdorf | D8ROE_1 | 380 | [6 empty] | 2504 | 2504 | 3150 | 2.6478 | 19.844 | 385.7876 | 82.808
Röhrsdorf - Remptendorf - Weida 573-575 | 11T0-0000-2138-C | 50HERTZ | Röhrsdorf | D8ROE_1 | Remptendorf | D8RE__1 | 380 | [6 empty] | 2504 |  |  | 4.2693 | 25.789 | 459.8349 | 103.396
Röhrsdorf - Remptendorf - Weida 574-576 | 11T0-0000-2142-Q | 50HERTZ | Röhrsdorf | D8ROE_1 | Remptendorf | D8RE__1 | 380 | [6 empty] | 2504 |  |  | 4.2693 | 25.789 | 459.8349 | 103.396
Streumen - Eula 585 | 11TD8L585------5 | 50HERTZ | Streumen | D8STR_1 | Eula | D8EU__1 | 380 | [6 empty] | 2520 |  |  | 2.9546 | 22.144 | 356.6964 | 84.359
Streumen - Eula 586 | 11TD8L586------Y | 50HERTZ | Streumen | D8STR_1 | Eula | D8EU__1 | 380 | [6 empty] | 2520 |  |  | 2.9546 | 22.144 | 356.6964 | 84.359
Eula - Pulgar 587 | 11TD8L587------Q | 50HERTZ | Eula | D8EU__1 | Pulgar | D8PUL_1 | 380 | [6 empty] | 2720 |  |  | 0.7639 | 4.9919 | 90.8549 | 20.185
Eula - Pulgar 588 | 11TD8L588------I | 50HERTZ | Eula | D8EU__1 | Pulgar | D8PUL_1 | 380 | [6 empty] | 2720 |  |  | 0.7639 | 4.9919 | 90.8549 | 20.185
Pulgar - Vieselbach 589 | 11TD8L589------A | 50HERTZ | Pulgar | D8PUL_1 | Vieselbach | D8VIB_1 | 380 | [6 empty] | 2520 |  |  | 3.2561 | 27.307 | 441.0796 | 104.4
Pulgar - Vieselbach 590 | 11TD8L590-----0Y | 50HERTZ | Pulgar | D8PUL_1 | Vieselbach | D8VIB_1 | 380 | [6 empty] | 2520 |  |  | 3.2561 | 27.307 | 441.0796 | 104.4
Dresden/Süd - Röhrsdorf 591 | 11TD8L591------S | 50HERTZ | Dresden/Süd | D8DRS_1 | Röhrsdorf | D8ROE_1 | 380 | [6 empty] | 2520 |  |  | 2.2251 | 22.06 | 380.6039 | 85.368
Dresden/Süd - Freiberg/Nord 592 | 11TD8L592------K | 50HERTZ | Dresden/Süd | D8DRS_1 | Freiberg/Nord | D8FRN_1 | 380 | [6 empty] | 2520 |  |  | 1.1724 | 12.37 | 212.9686 | 47.765
Freiberg/Nord - Röhrsdorf 594 | 11TD8L594------4 | 50HERTZ | Freiberg/Nord | D8FRN_1 | Röhrsdorf | D8ROE_1 | 380 | [6 empty] | 2520 |  |  | 1.0522 | 9.686 | 167.5726 | 37.587
Putlitz/Süd - Perleberg - Putlitz 596 | 11TD8L596------P | 50HERTZ | Putlitz/Süd | D8PZS_1 | Perleberg - Putlitz | D8PE__1 | 380 | [6 empty] | 2520 |  |  | 0.967 | 8.748 | 146.3354 | 34.208
Reuter - Mitte 903 | 11TD8L903------G | 50HERTZ | Reuter | D8REU_1 | Mitte | D8MIT_1 | 380 | [6 empty] | 800 |  |  | 0.267 | 2.372 | 769.6902 | 10.69
Reuter - Charlottenburg 904 | 11TD8L904------8 | 50HERTZ | Reuter | D8REU_1 | Charlottenburg | D8CH__1 | 380 | [6 empty] | 800 |  |  | 0.1291 | 1.2745 | 235.6194 | 5.27
Charlottenburg - Mitte 906 | 11TD8L906------T | 50HERTZ | Charlottenburg | D8CH__1 | Mitte | D8MIT_1 | 380 | [6 empty] | 800 |  |  | 0.1206 | 1.2301 | 475.0716 | 5.42
Teufelsbruch - Reuter 907 | 11TD8L907------L | 50HERTZ | Teufelsbruch | D8TB__1 | Reuter | D8REU_1 | 380 | [6 empty] | 1620 |  |  | 0.151 | 1.6912 | 690.2079 | 7.55
Teufelsbruch - Reuter 908 | 11TD8L908------D | 50HERTZ | Teufelsbruch | D8TB__1 | Reuter | D8REU_1 | 380 | [6 empty] | 1620 |  |  | 0.151 | 1.6912 | 690.2079 | 7.55
Friedrichshain - Mitte 919 | 11TD8L919------X | 50HERTZ | Friedrichshain | D8FRH_1 | Mitte | D8MIT_1 | 380 | [6 empty] | 1660 |  |  | 0.131 | 1.513 | 368.3203 | 6.55
Friedrichshain - Mitte 920 | 11TD8L920------M | 50HERTZ | Friedrichshain | D8FRH_1 | Mitte | D8MIT_1 | 380 | [6 empty] | 1660 |  |  | 0.131 | 1.5196 | 376.5513 | 6.55
Friedrichshain - Marzahn 921 | 11TD8L921------E | 50HERTZ | Friedrichshain | D8FRH_1 | Marzahn | D8MZA_1 | 380 | [6 empty] | 1660 |  |  | 0.1076 | 1.2266 | 300.8389 | 5.38
Friedrichshain - Marzahn 922 | 11TD8L922------6 | 50HERTZ | Friedrichshain | D8FRH_1 | Marzahn | D8MZA_1 | 380 | [6 empty] | 1660 |  |  | 0.1124 | 1.2145 | 321.0079 | 5.35
Hamburg/Nord - Brunsbüttel 951 | 11TD8L951------O | 50HERTZ | Hamburg/Nord | D8NOR_1 | Brunsbüttel | D8BRUH1 | 380 | [6 empty] | 3600 |  |  | 1.07 | 13.95 | 283.9371 | 57.098
Hamburg/Nord - Brunsbüttel 952 | 11TD8L952------G | 50HERTZ | Hamburg/Nord | D8NOR_1 | Brunsbüttel | D8BRUH1 | 380 | [6 empty] | 3600 |  |  | 1.07 | 13.95 | 283.9371 | 57.098
Hamburg/Ost - Hamburg/Nord 961 | 11TD8L961------F | 50HERTZ | Hamburg/Ost | D8OST_1 | Hamburg/Nord | D8NOR_1 | 380 | [6 empty] | 2580 | 2520 | 3300 | 1.0501 | 7.8803 | 139.204 | 31.001
Hamburg/Ost - Hamburg/Nord 962 | 11TD8L962------7 | 50HERTZ | Hamburg/Ost | D8OST_1 | Hamburg/Nord | D8NOR_1 | 380 | [6 empty] | 2580 | 2520 | 3300 | 1.0501 | 7.8803 | 139.204 | 31.001
Hamburg/Süd - Hamburg/Ost 971 | 11TD8L971------6 | 50HERTZ | Hamburg/Süd | D8SUE_1 | Hamburg/Ost | D8OST_1 | 380 | [6 empty] | 2580 |  |  | 0.9901 | 7.4404 | 131.9783 | 29.433
Hamburg/Ost - Krümmel 991 | 11TD8L991------P | 50HERTZ | Hamburg/Ost | D8OST_1 | Krümmel | D8KRU_1 | 380 | [6 empty] | 3600 |  |  | 0.59 | 6.7764 | 141.7172 | 28.392
Hamburg/Ost - Krümmel 992 | 11TD8L992------H | 50HERTZ | Hamburg/Ost | D8OST_1 | Krümmel | D8KRU_1 | 380 | [6 empty] | 3600 |  |  | 0.59 | 6.7764 | 141.7172 | 28.392
Ragow - Förderstedt 532 | 11TD8L532------0 | 50HERTZ | Ragow | D8RAG_1 | Förderstedt | D8FOE_1 | 380 | [6 empty] | 2520 |  |  | 4.9858 | 46.695 | 765.6061 | 179.426
Altdöbern - Streumen 563 | 11T0-0000-0949-E | 50HERTZ | Altdöbern | D8ADB_1 | Streumen | D8STR_1 | 380 | [6 empty] | 2500 |  |  | 1.7483 | 18.8461 | 312.274 | 70.533
Hamburg/Süd - Hamburg/Ost 972 | 11TD8L972------Z | 50HERTZ | Hamburg/Süd | D8SUE_1 | Hamburg/Ost | D8OST_1 | 380 | [6 empty] | 2580 |  |  | 0.9901 | 7.4404 | 131.9783 | 29.433
Putlitz/Süd - Stendal/West 515 | 11TD8L515------V | 50HERTZ | Putlitz/Süd | D8PZS_1 | Stendal/West | D8STW_1 | 380 | [6 empty] | 2520 |  |  | 2.0566 | 22.2964 | 369.1057 | 86.65
Vierraden - Neuenhagen 483 | 11T0-0000-0110-J | 50HERTZ | Vierraden | D8VIE_1 | Neuenhagen | D8NHG_1 | 380 | [6 empty] | 2720 |  |  | 2.363 | 22.445 | 442.509 | 92.255
Vierraden - Neuenhagen 484 | 11T0-0000-2031-1 | 50HERTZ | Vierraden | D8VIE_1 | Neuenhagen | D8NHG_1 | 380 | [6 empty] | 2720 |  |  | 2.363 | 22.445 | 442.509 | 92.255
Bertikow - Vierraden 481 | 11T0-0000-0109-X | 50HERTZ | Bertikow | D8BE__1 | Vierraden | D8VIE_1 | 380 | [6 empty] | 2720 |  |  | 0.815 | 8.067 | 162.672 | 33.644
Bertikow - Vierraden 482 | 11T0-0000-2030-4 | 50HERTZ | Bertikow | D8BE__1 | Vierraden | D8VIE_1 | 380 | [6 empty] | 2720 |  |  | 0.815 | 8.067 | 162.672 | 33.644
Pasewalk - Bertikow 407 | 11T0-0000-2035-Q | 50HERTZ | Pasewalk | D8PAS_1 | Bertikow | D8BE__1 | 380 | [6 empty] | 3600 |  |  | 0.5445 | 7.836 | 149.823 | 31.238
Pasewalk - Bertikow 408 | 11T0-0000-2036-N | 50HERTZ | Pasewalk | D8PAS_1 | Bertikow | D8BE__1 | 380 | [6 empty] | 3600 |  |  | 0.5445 | 7.836 | 149.823 | 31.238

## Tielines
|  |  | Substation_1 |  |  | Substation_2 |  |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters |  |  | TSO Share until border
NE_name | EIC_Code | TSO 1 | Full_name | Short_name | TSO 2 | Full_name | Short_name | Voltage_level [kV] | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Bentwisch - Bjaeverskov (DC cable) | 10T-DE-DK-00005A | 50HERTZ | Bentwisch | D8BWH_1 | Energinet.dk | Bjaeverskov | XBW_BJ1 | 400 | [6 empty] | 1500
Vierraden - Krajnik 507 | 10T-DE-PL-000039 | 50HERTZ | Vierraden | D8VIE_1 | PSE | Krajnik | XVI_KR1 | 380 | [6 empty] | 2520 |  |  | 0.35 | 3.49 | 57.177 | 13.1 | Tie-line to PL (PSE)
Vierraden - Krajnik 508 | 10T-DE-PL-000047 | 50HERTZ | Vierraden | D8VIE_1 | PSE | Krajnik | XVI_KR1 | 380 | [6 empty] | 2520 |  |  | 0.35 | 3.49 | 57.177 | 13.1 | Tie-line to PL (PSE)
Hagenwerder - Mikulowa 567 | 10T-DE-PL-00002B | 50HERTZ | Hagenwerder | D8HGW_1 | PSE | Mikulowa | XHG_MI1 | 380 | [6 empty] | 2520 |  |  | 0.233 | 2.53 | 28.7142 | 2.6 | Tie-line to PL (PSE)
Hagenwerder - Mikulowa 568 | 10T-DE-PL-00001D | 50HERTZ | Hagenwerder | D8HGW_1 | PSE | Mikulowa | XHG_MI1 | 380 | [6 empty] | 2520 |  |  | 0.243 | 2.606 | 29.8137 | 2.4 | Tie-line to PL (PSE)
Röhrsdorf - Hradec 445 | 10T-CZ-DE-00002U | 50HERTZ | Röhrsdorf | D8ROE_1 | CEPS | Hradec Vychod | XHR_RO1 | 380 | [6 empty] | 2520 |  |  | 1.23 | 10.945 | 174.8296 | 51.9 | Tie-line to CZ (CEPS)
Röhrsdorf - Hradec 446 | 10T-CZ-DE-00003S | 50HERTZ | Röhrsdorf | D8ROE_1 | CEPS | Hradec Vychod | XHR_RO1 | 380 | [6 empty] | 2520 |  |  | 1.23 | 10.945 | 174.8296 | 51.9 | Tie-line to CZ (CEPS)
Mecklar - Vieselbach 449-1 | 11T-D2-D8-000302 | TENNET | Mecklar | DME_VI1 | 50HERTZ | Vieselbach | D8VIB_1 | 380 | [6 empty] | 2520 |  |  | 1.774 | 16.325 | 267.067 | 87.1 | Tie-line to DE (TTG)
Mecklar - Eisenach 450-2 | 11T-D2-D8-000310 | TENNET | Mecklar | DME_EI1 | 50HERTZ | Eisenach | D8EI__1 | 380 | [6 empty] | 2520 |  |  | 0.833 | 6.886 | 139.801 | 15.6 | Tie-line to DE (TTG)
Krümmel - Krümmel 993 | 11T-D2-D8-00008W | 50HERTZ | Krümmel | D8KRU_1 | TENNET | Krümmel | DKR_KR1 | 380 | [6 empty] | 4000 |  |  | 0.004 | 0.2 | 0.031 | 0.2 | Tie-line to DE (TTG)
Krümmel - Krümmel 994 | 11T-D2-D8-00009U | 50HERTZ | Krümmel | D8KRU_1 | TENNET | Krümmel | DKR_KR1 | 380 | [6 empty] | 4000 |  |  | 0.004 | 0.2 | 0.031 | 0.2 | Tie-line to DE (TTG)
Hamburg/Süd - Dollern 981 | 11T-D2-D8-00063O | 50HERTZ | Hamburg/Süd | D8SUE_1 | TENNET | Dollern | DSU_DO1 | 380 | [6 empty] | 2280 |  |  | 0.457 | 3.548 | 71 | 28.6 | Tie-line to DE (TTG)
Hamburg/Süd - Dollern 982 | 11T-D2-D8-000051 | 50HERTZ | Hamburg/Süd | D8SUE_1 | TENNET | Dollern | DSU_DO1 | 380 | [6 empty] | 2280 |  |  | 0.457 | 3.548 | 71 | 28.6 | Tie-line to DE (TTG)
Brunsbüttel - Brunsbüttel 949 | 11T-D2-D8-000027 | 50HERTZ | Brunsbüttel | D8BRUH1 | TENNET | Brunsbüttel | D2BRUN1 | 380 | [6 empty] | 2100 |  |  | 0.002 | 0.2 | 0.346 | 0.2 | Tie-line to DE (TTG)
Altenfeld - Redwitz 459 | 11T-D2-D8-001007 | 50HERTZ | Altenfeld | D8ATF_1 | TENNET | Redwitz | DAL_RE1 | 380 | [6 empty] | 3600 |  |  | 0.429 | 7.087 | 132.842 | 25.8 | Tie-line to DE (TTG)
Altenfeld - Redwitz 460 | 11T-D2-D8-001015 | 50HERTZ | Altenfeld | D8ATF_1 | TENNET | Redwitz | DAL_RE1 | 380 | [6 empty] | 3600 |  |  | 0.94244 | 14.1667 | 265.6845 | 25.8 | Tie-line to DE (TTG)
Helmstedt - Wolmirstedt 491-1 | 11T-D2-D8-000205 | TENNET | Helmstedt | DHE_WO1 | 50HERTZ | Wolmirstedt | D8WOL_1 | 380 | [6 empty] | 3600 |  |  | 0.871 | 6.527 | 104.961 | 46.9 | Tie-line to DE (TTG)
Helmstedt - Wolmirstedt 492-2 | 11T-D2-D8-000213 | TENNET | Helmstedt | DHE_WO1 | 50HERTZ | Wolmirstedt | D8WOL_1 | 380 | [6 empty] | 3600 |  |  | 0.87 | 6.527 | 104.961 | 46.9 | Tie-line to DE (TTG)
Redwitz - Remptendorf 413 | 11T-D2-D8-00050X | TENNET | Redwitz | DRE_RE1 | 50HERTZ | Remptendorf | D8RE__1 | 380 | [6 empty] | 3600 |  |  | 0.731 | 7.216 | 126.606 | 18.4 | Tie-line to DE (TTG)
Redwitz - Remptendorf 414 | 11T-D2-D8-00051V | TENNET | Redwitz | DRE_RE1 | 50HERTZ | Remptendorf | D8RE__1 | 380 | [6 empty] | 3600 |  |  | 0.731 | 7.216 | 126.606 | 18.4 | Tie-line to DE (TTG)

## Transformers
Location |  |  |  | Maximum Current Imax (A) primary |  |  | Voltage_level (kV) |  | Electrical Parameters (primary) at neutral tap |  |  |  | Phase Shifting Properties
Full Name | Short Name | EIC_Code | TSO | Min | Max | Fixed | Primary | Secondary | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B (µS) | Conductance_G (µS) | Taps used for RAO | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%) | Comment
TR Eula 220/400 401 | D8EU__1 | 11TD8T401EU12--E | 50HERTZ | 866 | 866 |  | 400 | 231 | 0.668 | 51.462 | -415.27 | 2.562 |  |  |  | 1.385 | 0
TR Güstrow 220/400 403 | D8GUE_1 | 11TD8T403GUE12-P | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.3328 | 22.5167 | -477.407 | 3.1252 |  |  |  | 1.273 | 0
TR Hamburg/Nord 220/400 405 | D8NOR_1 | 11TD8T405NOR12-5 | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.925 | 62.9265 | -0.5687 | 0.7688 |  |  |  | 1.231 | 0
TR Hamburg/Nord 220/400 406 | D8NOR_1 | 11TD8T406NOR12-Y | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.925 | 62.9265 | -0.5687 | 0.7688 |  |  |  | 1.231 | 0
TR Lubmin 220/400 405 | D8LUB_1 | 11T0-0000-0003-J | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.7375 | 67.022 | -0.547 | 0.75 |  |  |  | 1.231 | 0
TR Marzahn 220/400 401 | D8MZA_1 | 11TD8T401MZA12-Q | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.506 | 40.429 | -1.126 | 0.5437 |  |  |  | 1.231 | 0
TR Marzahn 220/400 402 | D8MZA_1 | 11TD8T402MZA12-I | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.506 | 40.429 | -1.126 | 0.5437 |  |  |  | 1.231 | 0
TR Neuenhagen 220/400 401 | D8NHG_1 | 11TD8T401NHG12-N | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.3328 | 22.5167 | -477.407 | 3.1252 |  |  |  | 1.273 | 0
TR Neuenhagen 220/400 402 | D8NHG_1 | 11TD8T402NHG12-F | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.3328 | 22.5167 | -477.407 | 3.1252 |  |  |  | 1.273 | 0
TR Remptendorf 220/400 401 | D8RE__1 | 11TD8T401RE12--J | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Remptendorf 220/400 402 | D8RE__1 | 11TD8T402RE12--B | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Röhrsdorf 220/400 402 | D8ROE_1 | 11TD8T402ROE12-T | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.3328 | 22.5167 | -477.407 | 3.1252 |  |  |  | 1.273 | 0
TR Röhrsdorf 220/400 403 | D8ROE_1 | 11TD8T403ROE12-T | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.3328 | 22.5167 | -477.407 | 3.1252 |  |  |  | 1.273 | 0
PST Röhrsdorf 441 | D8ROE_1 | 11T0-0000-0011-L | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.1 | 12.187 | -0.902 | 1.1065 | -10;10 | 90 | Symmetrical |  | 1.069
PST Röhrsdorf 442 | D8ROE_1 | 11T0-0000-0012-I | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.097 | 12.607 | -0.159 | 0.696 | -10;10 | 90 | Symmetrical |  | 1.069
TR Thyrow 220/400 401 | D8THY_1 | 11TD8T401THY12-2 | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0
PST Vierraden 441 | D8VIE_1 | 11T0-0000-0013-F | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.1 | 12.187 | -0.902 | 1.1065 | -10;10 | 90 | Symmetrical |  | 1.069
PST Vierraden 443 | D8VIE_1 | 11T0-0000-0014-C | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.097 | 12.607 | -0.159 | 0.696 | -10;10 | 90 | Symmetrical |  | 1.069
TR Vieselbach 220/400 402 | D8VIB_1 | 11TD8T402VIB12-B | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Vieselbach 220/400 403 | D8VIB_1 | 11TD8T403VIB12-B | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Wolmirstedt 220/400 404 | D8WOL_1 | 11TD8T404WOL12-H | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Wustermark 220/400 401 | D8WU__1 | 11TD8T401WU12-0Y | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.703 | 64.88 | -0.671 | 0.775 |  |  |  | 1.231 | 0
TR Wustermark 220/400 402 | D8WU__1 | 11TD8T402WU12--S | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0
PST Hamburg/Ost 441 | D8OST_1 | 11T0-0000-1900-E | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.1 | 12.187 | -0.902 | 1.1065 | -10;10 | 90 | Symmetrical |  | 1.069
PST Hamburg/Ost 442 | D8OST_1 | 11T0-0000-1901-B | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.1 | 12.187 | -0.902 | 1.1065 | -10;10 | 90 | Symmetrical |  | 1.069
PST Hamburg/Ost 443 | D8OST_1 | 11T0-0000-1902-8 | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.097 | 12.607 | -0.159 | 0.696 | -10;10 | 90 | Symmetrical |  | 1.069
PST Hamburg/Ost 444 | D8OST_1 | 11T0-0000-1903-5 | 50HERTZ | 1690 | 1690 |  | 410 | 410 | 0.097 | 12.607 | -0.159 | 0.696 | -10;10 | 90 | Symmetrical |  | 1.069
TR Pasewalk 220/400 404 | D8PAS_1 | 11T0-0000-2086-3 | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.703 | 64.88 | -0.671 | 0.775 |  |  |  | 1.231 | 0
TR Pasewalk 220/400 405 | D8PAS_1 | 11T0-0000-2087-0 | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.917 | 63.193 | -0.75 | 1 |  |  |  | 1.231 | 0

## Remedial Actions
Location
Name of RA | TSO | Description
PST Roehrsdorf 441 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Roehrsdorf
PST Roehrsdorf 442 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Roehrsdorf
PST Vierraden 441 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Vierraden
PST Vierraden 443 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Vierraden
PST Hamburg/Ost 441 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Hamburg/Ost
PST Hamburg/Ost 442 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Hamburg/Ost
PST Hamburg/Ost 443 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Hamburg/Ost
PST Hamburg/Ost 444 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Hamburg/Ost